## Sheet1
Short name | Long name | OBIS reference | Attribute | Class ID | Value Format | Value Unit
P1Version | Version information for P1 output | 1-3:0.2.8.255 | 2 | 1 Data | S2, tag 9
DateTimeElectric | Date-time stamp of the P1 message | 0-0:1.0.0.255 | 2 | 8 | TST | YYMMDDhhmmssX
EquipmentIDElectric | Equipment identifier | 0-0:96.1.1.255 | 2 Value | 1 Data | Sn (n=0..96), tag 9
ElectricityToClient(1) | Meter Reading electricity delivered to client (Tariff 1) in 0,001 kWh | 1-0:1.8.1.255 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
ElectricityToClient(2) | Meter Reading electricity delivered to client (Tariff 2) in 0,001 kWh | 1-0:1.8.2.255 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
ElectricityByClient(1) | Meter Reading electricity delivered by client (Tariff 1) in 0,001 kWh | 1-0:2.8.1.255 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
ElectricityByClient(2) | Meter Reading electricity delivered by client (Tariff 2) in 0,001 kWh | 1-0:2.8.2.255 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
TariffIndicator | Tariff indicator elec- tricity. The tariff in- dicator can also be used to switch tariff dependent loads e.g boilers. This is the responsibility of the P1 user | 0-0:96.14.0.255 | 2 Value | 1 Data | S4, tag 9
ActualElectricityToClient | Actual electricity power delivered (+P) in 1 Watt resolution | 1-0:1.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
ActualElectricityByClient | Actual electricity power received (-P) in 1 Watt resolution | 1-0:2.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
NPowerFailuresAny | Number of power failures in any phase | 0-0:96.7.21.255 | 2 Value | 1 Data | F5(0,0), tag 18
NLongPowerFailuresAny | Number of long power failures in any phase | 0-0:96.7.9.255 | 2 Value | 1 Data | F5(0,0), tag 18
LongPowerFailureLog | Power Failure Event Log (long power failures) | 1-0:99.97.0.255 | 2 Buffer | 7 Profile Ge- neric | TST, F10(0,0) - tag 6 Format applicable for the value within the log (OBIS code 0-0:96.7.19.255) | Timestamp (end of failure) – duration in seconds
NSagsL1 | Number of voltage sags in phase L1 | 1-0:32.32.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
NSagsL2 | Number of voltage sags in phase L2 | 1-0:52.32.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
NSagsL3 | Number of voltage sags in phase L3 | 1-0:72.32.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
NSwellsL1 | Number of voltage swells in phase L1 | 1-0:32.36.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
NSwellsL2 | Number of voltage swells in phase L2 | 1-0:52.36.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
NSwellsL3 | Number of voltage swells in phase L3 | 1-0:72.36.0.255 | 2 Value | 1 Data | F5(0,0), tag 18
Message | Text message max 1024 characters. | 0-0:96.13.0.255 | 2 Value | 1 Data | Sn (n=0..2048), tag 9
InstantVoltageL1 | Instantaneous voltage L1 in V resolution | 1-0:32.7.0.255 | 2 Value |  | F4(1,1), tag 18 | V
InstantVoltageL2 | Instantaneous voltage L2 in V resolution | 1-0:52.7.0.255 | 2 Value | 3 Register | F4(1,1), tag 18 | V
InstantVoltageL3 | Instantaneous voltage L3 in V resolution | 1-0:72.7.0.255 | 2 Value | 3 Register | F4(1,1), tag 18 | V
InstantCurrentL1 | Instantaneous current L1 in A resolution | 1-0:31.7.0.255 | 2 Value | 3 Register | F3(0,0), tag 18 | A
InstantCurrentL2 | Instantaneous current L2 in A resolution | 1-0:51.7.0.255 | 2 Value | 3 Register | F3(0,0), tag 18 | A
InstantCurrentL3 | Instantaneous current L3 in A resolution | 1-0:71.7.0.255 | 2 Value | 3 Register | F3(0,0), tag 18 | A
Instant+PowerL1 | Instantaneous active power L1 (+P) in W resolution | 1-0:21.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instant+PowerL2 | Instantaneous active power L2 (+P) in W resolution | 1-0:41.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instant+PowerL3 | Instantaneous active power L3 (+P) in W resolution | 1-0:61.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instant-PowerL1 | Instantaneous active power L1 (-P) in W resolution | 1-0:22.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instant-PowerL2 | Instantaneous active power L2 (-P) in W resolution | 1-0:42.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instant-PowerL3 | Instantaneous active power L3 (-P) in W resolution | 1-0:62.7.0.255 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
DeviceTypeGas | Device-Type | 0-1:24.1.0.255 | 9 Device type | 72 M-Bus client | F3(0,0), tag 17
EquipmentIDGas | Equipment identifier (Gas) | 0-1:96.1.0.255 | 2 Value | 1 Data | Sn (n=0..96), tag 9
DateTimeGas | Last 5-minute value (temperature con- verted), gas delivered to client in m3, including decimal values and capture time | 0-1:24.2.1.255 | 5 Capture time | 4 Extended Register | TST
GasToClient |  | 0-1:24.2.1.255 | 2 Value | 4 Extended Register | F8(2,2)/F8(3,3), tag 18 (See note 2) | m3
DeviceTypeThermal | Device-Type | 0-2:24.1.0.255 | 9 Device type | 72 M-Bus cli- ent | F3(0,0), tag 17
EquipmentIDThermal | Equipment identifier (Thermal: Heat or Cold) | 0-2:96.1.0.255 | 2 Value | 1 Data | Sn (n=0..96), tag 9
DateTimeThermal | Last 5-minute Meter reading Heat or Cold in 0,01 GJ and capture time | 0-2:24.2.1.255 | 5 Capture time | 4 Extended Register | TST
ThermalToClient |  | 0-2:24.2.1.255 | 2 Value | 4 Extended Register | Fn(2,2) (See note 1) | GJ
DeviceTypeWater | Device-Type | 0-3:24.1.0.255 | 9 Device type | 72 M-Bus cli- ent | F3(0,0), tag 17
EquipmentIDWater | Equipment identifier (Water) | 0-3:96.1.0.255 | 2 Value | 1 Data | Sn (n=0..96), tag 9
DateTimeWater | Last 5-minute Meter reading in 0,001 m3 and capture time | 0-3:24.2.1.255 | 5 Capture time | 4 Extended Register | TST
WaterToClient |  | 0-3:24.2.1.255 | 2 Value | 4 Extended Register | Fn(2,2) (See note 1) | m3
DeviceTypeSlave | Device-Type | 0-4:24.1.0.255 | 9 Device type | 72 M-Bus cli- ent | F3(0,0), tag 17
EquipmentIDSlave | Equipment identifier | 0-4:96.1.0.255 | 2 Value | 1 Data | Sn (n=0..96), tag 9
DateTimeSlave | Last 5-minute Meter reading and capture time (e.g. slave E meter) | 0-4:24.2.1.255 | 5 Capture time | 4 Extended Register | TST
SlaveToClient |  | 0-4:24.2.1.255 | 2 Value | 4 Extended Register | Fn(2,2) (See note 1) | kWh